# On-Site Wastewater Treatment Plant for Jakob Village

In El-Fashn – Bani Suef Governorate

Starting up results

- The Treatment Plant

The treatment unit contains declination chamber with galvanized steel screen, three parallel settling tanks that receives wastewater from the screen, settles the settable solids. Water stay 2-8 hours in the settling tanks then goes to air injection chamber to increase Oxygen for the bacteria. Water leaves to Gravel Bed Hydroponics Filters that treats the organic matters by aerobic bacteria. Clear water then goes to shallow maturation pond for solar treatment then goes to the drain. The sludge produced in the settling tanks spreads and dried in drying beds, the drainage water from the drying beds collects in a sump that contains portable submersible pump to deliver water to the air injection chamber.

To through treated wastewater to any drain, water quality must be according to the Egyptian law

Egyptian law parameters that allow to through treated water to the drain are shown in the following table.

| Temperature ° C | Less than 35 |
| --- | --- |
| PH | 6-9 |
| BOD mg/l | 60 |
| COD mg/l | 80 |
| DO mg/l | Not less than 4 |
| TDS mg/l | 2000 |
| TSS mg/l | 50 |

Bani Suef Water and Wastewater Company is responsible for operating and maintenance these systems, so we asked them to follow up the treatment results from Jakob wastewater treatment plant after starting up the plant the started taking samples from 24, February 2010 and the following table show the history of the results of Jakob wastewater treatment plant

Treatment plant started up on first of January 2010

| Date | Raw water (influent) | Effluent |
| --- | --- | --- |
|  | Temp ° C | PH | BOD mg/l | COD mg/l | DO mg/l | TDS mg/l | TSS mg/l | Temp ° C | PH | BOD mg/l | COD mg/l | DO mg/l | TDS mg/l | TSS mg/l |
| 24/2/2010 | 23.1 | 7.1 | 300 | 538 |  | 536 | 324 | 22.8 | 8.5 | 41 | 140 | 4.2 | 612 | 84 |
| 31/3/2010 | 23.2 | 7.5 | NA | 568 |  | 660 | 224 | 23.8 | 8.0 | NA | 103 | 4.0 | 776 | 56 |
| 20/4/2010 | 29.4 | 7.19 | 538 | 985 |  | 954 | 344 | 32.5 | 8.05 | 52 | 77 | 4.5 | 732 | 26 |
| 25/5/2010 | 26.2 | 7.2 | 540 | 980 |  | 960 | 350 | 27.5 | 8.3 | 45 | 70 | 4.3 | 750 | 25 |
| 20/6/2010 | 27.5 | 7.5 | 520 | 960 |  | 980 | 320 | 28.1 | 8.2 | 41 | 66 | 4.2 | 820 | 22 |
| 22/7/2010 | 29.5 | 7.3 | 570 | 955 |  | 1100 | 360 | 28.5 | 8.2 | 50 | 68 | 4.1 | 815 | 35 |
| 20/8/2010 | 29.3 | 7.2 | 502 | 940 |  | 985 | 340 | 28.3 | 8.1 | 38 | 62 | 4.3 | 810 | 32 |
| 22/9/2010 | 28.5 | 7.4 | 530 | 970 |  | 1200 | 332 | 28.5 | 8.3 | 50 | 55 | 4.2 | 750 | 60 |
| 20/10/2010 | 29.1 | 7.2 | 490 | 890 |  | 986 | 328 | 27.9 | 8.2 | 45 | 51 | 4.5 | 735 | 42 |

Result analysis

The treatment plant results is improving from month to month according to growing the reed plant in the gravel bed filters and the following table shows the organics percentage removal

| Date | BOD removal % | COD removal % | TSS removal % |
| --- | --- | --- | --- |
| 24/2/2010 | 86.3 | 74.0 | 74.1 |
| 31/3/2010 | NA | 81.9 | 75.0 |
| 20/4/2010 | 90.3 | 92.2 | 92.4 |
| 25/5/2010 | 91.7 | 92.9 | 92.9 |
| 20/6/2010 | 92.1 | 93.1 | 93.1 |
| 22/7/2010 | 91.2 | 92.9 | 90.3 |
| 20/8/2010 | 92.4 | 93.4 | 90.6 |
| 22/9/2010 | 90.6 | 94.3 | 81.9 |
| 20/10/2010 | 90.8 | 94.3 | 87.2 |

ADVANTAGES OF THE SYSTEM

- Minimal land requirement

- Harmonious with nature in appearance and dynamics

- Proven technology

- Cost of operation and maintenance lower than traditional technology

- Good pathogen removal from die-off and natural biological processes

- Effective with a wide range of water plants

- High levels of treatment possible by increasing planted area

- Uses gravity feed to reduce use of energy