## Hidraulica
COMENSA TOPOGRAFIA | [5 empty] | Kalompatzom | [7 empty] | Flow (Ql/s) | 1.1
ALDEA: |  |  |  |  | FECHA: | 8 de junio | [7 empty] | tap (l/s) : | 0.1
MUNICIPIO: |  | Cotzol |  |  | TECNICOS. | Taylor Dibbert y Diego Ramirez
Punto | Segm. | Distance. | orient | angle | delta | Relative altitude | North (m) | East (m) | houses provided | tap still to be delivered | mojon | HGL for graph(m) | Diam (mm) | Cauldal-L/SEG | Tanks | Residual Head (m) | Static Head (m) | velocidad (m/s)
AA-0 | 0 | 0 | 0 | 0 | 0 | 1000 | 0 | 0 |  |  | NACIMIENTO 1 | 1000 | 66 | 1.1 |  | 0 | 0
AA-1 | 21.3 | 21.3 | 76 | -21 | -7.6332 | 992.3668 | 4.8107 | 19.2946 |  |  |  | 1000 | 66 | 1.1 |  | 7.6332 | 7.6332 | 0.32153
AA-2 | 14.3 | 35.6 | 75 | -29 | -6.9328 | 985.434 | 8.0477 | 31.3755 |  |  |  | 999.9723 | 66 | 1.1 |  | 14.5383 | 14.566 | 0.32153
AA-3 | 7.5 | 43.1 | 52 | -38 | -4.6175 | 980.8165 | 11.6864 | 36.0327 |  |  | puente HG 12m | 999.9578 | 66 | 1.1 |  | 19.1413 | 19.1835 | 0.32153
AA-4 | 5.4 | 48.5 | 40 | -6.5 | -0.6113 | 980.2052 | 15.7964 | 39.4814 |  |  | rio (5.4 m ancho)/ 2 codos de 45* | 999.9473 | 66 | 1.1 |  | 19.7421 | 19.7948 | 0.32153
AA-5 | 9 | 57.5 | 58 | 45 | 6.364 | 986.5692 | 19.1688 | 44.8784 |  |  |  | 999.9299 | 66 | 1.1 |  | 13.3607 | 13.4308 | 0.32153
AA-6 | 6.5 | 64 | 86 | 30 | 3.25 | 989.8192 | 19.5615 | 50.4938 |  |  |  | 999.9173 | 66 | 1.1 |  | 10.0981 | 10.1808 | 0.32153
AA-7 | 12.6 | 76.6 | 58 | 14 | 3.0482 | 992.8674 | 26.0401 | 60.8618 |  |  | rio pequeño 6 HG | 999.8929 | 66 | 1.1 |  | 7.0255 | 7.1326 | 0.32153
AA-8 | 6.2 | 82.8 | 92 | 0 | 0 | 992.8674 | 25.8237 | 67.0581 |  |  | rio pequeño con piedras 6m HG | 999.8809 | 66 | 1.1 |  | 7.0135 | 7.1326 | 0.32153
AA-9 | 6.2 | 89 | 101 | 7 | 0.75559 | 993.623 | 24.6495 | 73.0988 |  |  |  | 999.8689 | 66 | 1.1 |  | 6.2459 | 6.377 | 0.32153
AA-10 | 10.1 | 99.1 | 100 | -4 | -0.70454 | 992.9185 | 22.9 | 83.0211 |  |  |  | 999.8493 | 66 | 1.1 |  | 6.9309 | 7.0815 | 0.32153
AA-11 | 17.7 | 116.8 | 93 | 0 | 0 | 992.9185 | 21.9736 | 100.6968 |  |  |  | 999.815 | 66 | 1.1 |  | 6.8966 | 7.0815 | 0.32153
AA-12 | 15.2 | 132 | 82 | -4 | -1.0603 | 991.8582 | 24.0839 | 115.7123 |  |  |  | 999.7495 | 56 | 1.1 |  | 7.8914 | 8.1418 | 0.32153
AA-13 | 15.8 | 147.8 | 86 | -3.5 | -0.96457 | 990.8936 | 25.184 | 131.4444 |  |  | perfil U codo 45ª PVC | 999.6814 | 56 | 1.1 |  | 8.7878 | 9.1064 | 0.44661
AA-14 | 12.3 | 160.1 | 108 | 2 | 0.42926 | 991.3229 | 21.3854 | 143.1352 |  |  |  | 999.6284 | 56 | 1.1 |  | 8.3055 | 8.6771 | 0.44661
AA-15 | 10.4 | 170.5 | 108 | 0 | 0 | 991.3229 | 18.1716 | 153.0262 |  |  |  | 999.5836 | 56 | 1.1 |  | 8.2607 | 8.6771 | 0.44661
AA-16 | 7.4 | 177.9 | 115 | 5 | 0.64495 | 991.9678 | 15.0561 | 159.7074 |  |  | 6m HG | 999.5517 | 56 | 1.1 |  | 7.5839 | 8.0322 | 0.44661
AA-17 | 6.9 | 184.8 | 96 | 4 | 0.48132 | 992.4491 | 14.3367 | 166.5529 |  |  |  | 999.5219 | 56 | 1.1 |  | 7.0728 | 7.5509 | 0.44661
AA-18 | 10.6 | 195.4 | 96 | -0.5 | -0.092501 | 992.3566 | 13.2287 | 177.0944 |  |  |  | 999.4762 | 56 | 1.1 |  | 7.1196 | 7.6434 | 0.44661
AA-19 | 17.2 | 212.6 | 56 | -6.5 | -1.9471 | 990.4095 | 22.785 | 191.2622 |  |  |  | 999.4021 | 56 | 1.1 |  | 8.9925 | 9.5905 | 0.44661
AA-20 | 11.5 | 224.1 | 78 | 1 | 0.2007 | 990.6102 | 25.1756 | 202.5092 |  |  |  | 999.3525 | 56 | 1.1 |  | 8.7423 | 9.3898 | 0.44661
AA-21 | 23.2 | 247.3 | 98 | -1.5 | -0.60731 | 990.0029 | 21.9479 | 225.4755 |  |  |  | 999.2525 | 56 | 1.1 |  | 9.2496 | 9.9971 | 0.44661
AA-22 | 15.3 | 262.6 | 98 | 2 | 0.53396 | 990.5369 | 19.8198 | 240.6174 |  |  |  | 999.1865 | 56 | 1.1 |  | 8.6496 | 9.4631 | 0.44661
AA-23 | 13.2 | 275.8 | 120 | 3 | 0.69083 | 991.2277 | 13.2289 | 252.0333 |  |  |  | 999.1296 | 56 | 1.1 |  | 7.9019 | 8.7723 | 0.44661
AA-24 | 10.4 | 286.2 | 112 | 17 | 3.0407 | 994.2684 | 9.5032 | 261.2546 |  |  |  | 999.0848 | 56 | 1.1 |  | 4.8164 | 5.7316 | 0.44661
AA-25 | 15.2 | 301.4 | 80 | -19 | -4.9486 | 989.3198 | 11.9989 | 275.4082 |  |  |  | 999.0193 | 56 | 1.1 |  | 9.6995 | 10.6802 | 0.44661
AA-26 | 13 | 314.4 | 58 | 1 | 0.22688 | 989.5466 | 18.8868 | 286.4311 |  |  |  | 998.9632 | 56 | 1.1 |  | 9.4166 | 10.4534 | 0.44661
AA-27 | 14.3 | 328.7 | 68 | -4 | -0.99752 | 988.5491 | 24.2306 | 299.6575 |  |  |  | 998.9016 | 56 | 1.1 |  | 10.3525 | 11.4509 | 0.44661
AA-28 | 11.3 | 340 | 86 | 1 | 0.19721 | 988.7463 | 25.0187 | 310.9283 |  |  |  | 998.8529 | 56 | 1.1 |  | 10.1065 | 11.2537 | 0.44661
AA-29 | 11 | 351 | 69 | -7.5 | -1.4358 | 987.3105 | 28.927 | 321.1098 |  |  | rodear roca (6m HG) | 998.8055 | 56 | 1.1 |  | 11.4949 | 12.6895 | 0.44661
AA-30 | 17.4 | 368.4 | 79 | 1.5 | 0.45548 | 987.766 | 32.246 | 338.1843 |  |  |  | 998.7304 | 56 | 1.1 |  | 10.9644 | 12.234 | 0.44661
AA-31 | 21.3 | 389.7 | 79 | -1 | -0.37174 | 987.3943 | 36.3096 | 359.0898 |  |  |  | 998.6386 | 56 | 1.1 |  | 11.2443 | 12.6057 | 0.44661
AA-32 | 10.9 | 400.6 | 76 | -0.5 | -0.095119 | 987.2992 | 38.9464 | 369.6656 |  |  |  | 998.5916 | 56 | 1.1 |  | 11.2925 | 12.7008 | 0.44661
AA-33 | 13.1 | 413.7 | 28 | -5 | -1.1417 | 986.1574 | 50.469 | 375.7923 |  |  | empieza campo de milpa | 998.5352 | 56 | 1.1 |  | 12.3777 | 13.8426 | 0.44661
AA-34 | 7 | 420.7 | 54 | -5 | -0.61009 | 985.5473 | 54.5679 | 381.4338 |  |  | milpa | 998.505 | 56 | 1.1 |  | 12.9577 | 14.4527 | 0.44661
AA-35 | 7.8 | 428.5 | 64 | -3 | -0.40822 | 985.1391 | 57.9825 | 388.4348 |  |  | milpa | 998.4714 | 56 | 1.1 |  | 13.3323 | 14.8609 | 0.44661
AA-36 | 6.5 | 435 | 64 | 2.5 | 0.28353 | 985.4226 | 60.8292 | 394.2714 |  |  | milpa | 998.4433 | 56 | 1.1 |  | 13.0207 | 14.5774 | 0.44661
AA-37 | 8.1 | 443.1 | 64 | -3.5 | -0.49449 | 984.9281 | 64.3734 | 401.5381 |  |  | milpa | 998.4084 | 56 | 1.1 |  | 13.4803 | 15.0719 | 0.44661
AA-38 | 5.7 | 448.8 | 52 | 3.5 | 0.34798 | 985.2761 | 67.8761 | 406.0214 |  |  | milpa | 998.3839 | 56 | 1.1 |  | 13.1077 | 14.7239 | 0.44661
AA-39 | 7 | 455.8 | 44 | 4 | 0.4883 | 985.7644 | 72.8992 | 410.8721 |  |  | milpa | 998.3537 | 56 | 1.1 |  | 12.5893 | 14.2356 | 0.44661
AA-40 | 8.4 | 464.2 | 58 | 5 | 0.73211 | 986.4965 | 77.3336 | 417.9686 |  |  | milpa | 998.3175 | 56 | 1.1 |  | 11.8209 | 13.5035 | 0.44661
AA-41 | 5.5 | 469.7 | 62 | 10 | 0.95506 | 987.4516 | 79.8765 | 422.751 |  |  | fin milpa potrero | 998.2938 | 56 | 1.1 |  | 10.8422 | 12.5484 | 0.44661
AA-42 | 16 | 485.7 | 95 | -13 | -3.5992 | 983.8524 | 78.5177 | 438.2816 |  |  | potrero | 998.2248 | 56 | 1.1 |  | 14.3724 | 16.1476 | 0.44661
AA-43 | 17.5 | 503.2 | 105 | -10 | -3.0388 | 980.8135 | 74.0572 | 454.9285 |  |  |  | 998.1494 | 56 | 1.1 |  | 17.3358 | 19.1865 | 0.44661
AA-44 | 16 | 519.2 | 103 | -7.5 | -2.0884 | 978.7251 | 70.4888 | 470.3851 |  |  |  | 998.0804 | 56 | 1.1 |  | 19.3553 | 21.2749 | 0.44661
AA-45 | 18.8 | 538 | 106 | -4 | -1.3114 | 977.4137 | 65.3194 | 488.4128 |  |  |  | 997.9993 | 56 | 1.1 |  | 20.5856 | 22.5863 | 0.44661
AA-46 | 15 | 553 | 105 | 0 | 0 | 977.4137 | 61.4371 | 502.9017 |  |  |  | 997.9347 | 56 | 1.1 |  | 20.521 | 22.5863 | 0.44661
AA-47 | 16.3 | 569.3 | 102 | -6 | -1.7038 | 975.7099 | 58.0667 | 518.7581 |  |  | potrero | 997.8644 | 56 | 1.1 |  | 22.1545 | 24.2901 | 0.44661
AA-48 | 13.7 | 583 | 102 | 2 | 0.47812 | 976.188 | 55.2201 | 532.1506 |  |  |  | 997.8054 | 56 | 1.1 |  | 21.6174 | 23.812 | 0.44661
AA-49 | 10.4 | 593.4 | 100 | -1 | -0.18151 | 976.0065 | 53.4144 | 542.391 |  |  | preguntar Diego | 997.7605 | 56 | 1.1 |  | 21.754 | 23.9935 | 0.44661
AA-50 | 14.8 | 608.2 | 92 | -1 | -0.2583 | 975.7482 | 52.898 | 557.1798 |  |  |  | 997.6967 | 56 | 1.1 |  | 21.9485 | 24.2518 | 0.44661
AA-51 | 12.4 | 620.6 | 88 | -0.5 | -0.10821 | 975.64 | 53.3307 | 569.5717 |  |  |  | 997.6433 | 56 | 1.1 |  | 22.0033 | 24.36 | 0.44661
AA-52 | 13.4 | 634 | 88 | -0.5 | -0.11694 | 975.5231 | 53.7983 | 582.9631 |  |  |  | 997.5855 | 56 | 1.1 |  | 22.0624 | 24.4769 | 0.44661
AA-53 | 12.4 | 646.4 | 102 | -0.5 | -0.10821 | 975.4148 | 51.2203 | 595.0916 |  |  |  | 997.532 | 56 | 1.1 |  | 22.1172 | 24.5852 | 0.44661
AA-54 | 10.3 | 656.7 | 100 | 4 | 0.71849 | 976.1333 | 49.4361 | 605.2104 |  |  |  | 997.4876 | 56 | 1.1 |  | 21.3543 | 23.8667 | 0.44661
AA-55 | 12 | 668.7 | 79 | -1.5 | -0.31412 | 975.8192 | 51.725 | 616.9859 |  |  |  | 997.4359 | 56 | 1.1 |  | 21.6167 | 24.1808 | 0.44661
AA-56 | 12.5 | 681.2 | 82 | -1 | -0.21816 | 975.6011 | 53.4644 | 629.3624 |  |  |  | 997.382 | 56 | 1.1 |  | 21.781 | 24.3989 | 0.44661
AA-57 | 7.9 | 689.1 | 92 | 2 | 0.27571 | 975.8768 | 53.1889 | 637.2528 |  |  |  | 997.348 | 56 | 1.1 |  | 21.4712 | 24.1232 | 0.44661
AA-58 | 9 | 698.1 | 112 | 12 | 1.8712 | 977.748 | 49.8911 | 645.4151 |  |  | 6m HG | 997.3092 | 56 | 1.1 |  | 19.5612 | 22.252 | 0.44661
AA-59 | 13.2 | 711.3 | 95 | -3 | -0.69083 | 977.0571 | 48.7422 | 658.5468 |  |  |  | 997.2523 | 56 | 1.1 |  | 20.1951 | 22.9429 | 0.44661
AA-60 | 9 | 720.3 | 108 | 2 | 0.3141 | 977.3712 | 45.9628 | 667.1011 |  |  |  | 997.2135 | 56 | 1.1 |  | 19.8422 | 22.6288 | 0.44661
AA-61 | 12.8 | 733.1 | 97 | 4 | 0.89288 | 978.2641 | 44.4066 | 679.7748 |  |  |  | 997.1583 | 56 | 1.1 |  | 18.8942 | 21.7359 | 0.44661
AA-62 | 13.1 | 746.2 | 96 | 1 | 0.22863 | 978.4927 | 43.0375 | 692.801 |  |  |  | 997.1018 | 56 | 1.1 |  | 18.6091 | 21.5073 | 0.44661
AA-63 | 14.3 | 760.5 | 110 | 6.5 | 1.6188 | 980.1115 | 38.1781 | 706.1523 |  |  | codo 45* PVC | 997.0402 | 56 | 1.1 |  | 16.9286 | 19.8885 | 0.44661
AA-64 | 6 | 766.5 | 122 | -5 | -0.52293 | 979.5886 | 35.0107 | 711.2212 |  |  |  | 997.0143 | 56 | 1.1 |  | 17.4257 | 20.4114 | 0.44661
AA-65 | 6 | 772.5 | 105 | 10 | 1.0419 | 980.6305 | 33.4813 | 716.9287 |  |  |  | 996.9885 | 56 | 1.1 |  | 16.358 | 19.3695 | 0.44661
AA-66 | 16.5 | 789 | 64 | -5.5 | -1.5815 | 979.049 | 40.6812 | 731.6905 |  |  |  | 996.9173 | 56 | 1.1 |  | 17.8683 | 20.951 | 0.44661
AA-67 | 11 | 800 | 56 | 5 | 0.95871 | 980.0078 | 46.8089 | 740.7752 |  |  |  | 996.8699 | 56 | 1.1 |  | 16.8621 | 19.9922 | 0.44661
AA-68 | 16 | 816 | 46 | -5 | -1.3945 | 978.6133 | 57.8811 | 752.2409 |  |  |  | 996.8009 | 56 | 1.1 |  | 18.1877 | 21.3867 | 0.44661
AA-69 | 20 | 836 | 50 | 1 | 0.34905 | 978.9623 | 70.7349 | 767.5594 |  |  |  | 996.7147 | 56 | 1.1 |  | 17.7524 | 21.0377 | 0.44661
AA-70 | 16 | 852 | 69 | 0.5 | 0.13962 | 979.1019 | 76.4686 | 782.4961 |  |  |  | 996.6457 | 56 | 1.1 |  | 17.5438 | 20.8981 | 0.44661
AA-71 | 12 | 864 | 69 | -3.5 | -0.73258 | 978.3694 | 80.761 | 793.6782 |  |  |  | 996.594 | 56 | 1.1 |  | 18.2247 | 21.6306 | 0.44661
AA-72 | 15.2 | 879.2 | 69 | 1 | 0.26528 | 978.6346 | 86.2073 | 807.8665 |  |  |  | 996.5285 | 56 | 1.1 |  | 17.8939 | 21.3654 | 0.44661
AA-73 | 13.1 | 892.3 | 73 | 1 | 0.22863 | 978.8633 | 90.0368 | 820.3922 |  |  |  | 996.472 | 56 | 1.1 |  | 17.6088 | 21.1367 | 0.44661
AA-74 | 7.5 | 899.8 | 52 | -6 | -0.78396 | 978.0793 | 94.629 | 826.2699 |  |  |  | 996.4397 | 56 | 1.1 |  | 18.3604 | 21.9207 | 0.44661
AA-75 | 16.2 | 916 | 38 | 1 | 0.28273 | 978.362 | 107.3928 | 836.2421 |  |  |  | 996.3699 | 56 | 1.1 |  | 18.0078 | 21.638 | 0.44661
AA-76 | 18 | 934 | 84 | -0.5 | -0.15708 | 978.2049 | 109.2743 | 854.1428 |  |  |  | 996.2923 | 56 | 1.1 |  | 18.0873 | 21.7951 | 0.44661
AA-77 | 13 | 947 | 97 | 7 | 1.5843 | 979.7892 | 107.7018 | 866.9497 |  |  |  | 996.2362 | 56 | 1.1 |  | 16.447 | 20.2108 | 0.44661
AA-78 | 14 | 961 | 94 | -8 | -1.9484 | 977.8408 | 106.7347 | 880.7797 |  |  |  | 996.1759 | 56 | 1.1 |  | 18.335 | 22.1592 | 0.44661
AA-79 | 11.5 | 972.5 | 135 | -4 | -0.8022 | 977.0386 | 98.6228 | 888.8916 |  |  |  | 996.1263 | 56 | 1.1 |  | 19.0877 | 22.9614 | 0.44661
AA-80 | 11 | 983.5 | 135 | 14.5 | 2.7542 | 979.7928 | 91.0923 | 896.422 |  |  |  | 996.0789 | 56 | 1.1 |  | 16.2861 | 20.2072 | 0.44661
AA-81 | 10 | 993.5 | 144 | -21 | -3.5837 | 976.2091 | 83.5395 | 901.9095 |  |  | se va para abajo para rodear rocas | 996.0358 | 56 | 1.1 |  | 19.8266 | 23.7909 | 0.44661
AA-82 | 11 | 1004.5 | 138 | -14 | -2.6611 | 973.548 | 75.6077 | 909.0513 |  |  | 6m HG | 995.9883 | 56 | 1.1 |  | 22.4404 | 26.452 | 0.44661
AA-83 | 9.1 | 1013.6 | 138 | -1 | -0.15882 | 973.3892 | 67.2958 | 912.752 |  |  |  | 995.9491 | 56 | 1.1 |  | 22.5599 | 26.6108 | 0.44661
AA-84 | 12.3 | 1025.9 | 156 | 21 | 4.4079 | 977.7971 | 62.9941 | 923.3989 |  |  |  | 995.8961 | 56 | 1.1 |  | 18.099 | 22.2029 | 0.44661
AA-85 | 14.5 | 1040.4 | 112 | 14.5 | 3.6305 | 981.4276 | 64.2176 | 937.3836 |  |  |  | 995.8336 | 56 | 1.1 |  | 14.406 | 18.5724 | 0.44661
AA-86 | 8 | 1048.4 | 85 | 8 | 1.1134 | 982.541 | 62.9783 | 945.2082 |  |  |  | 995.7991 | 56 | 1.1 |  | 13.2581 | 17.459 | 0.44661
AA-87 | 10 | 1058.4 | 99 | 2 | 0.34899 | 982.89 | 57.3898 | 953.4935 |  |  |  | 995.756 | 56 | 1.1 |  | 12.866 | 17.11 | 0.44661
AA-88 | 16 | 1074.4 | 124 | 1 | 0.27924 | 983.1692 | 48.4441 | 966.7561 |  |  |  | 995.687 | 56 | 1.1 |  | 12.5178 | 16.8308 | 0.44661
AA-89 | 15 | 1089.4 | 124 | 11 | 2.8621 | 986.0314 | 37.5017 | 976.6087 |  |  |  | 995.6224 | 56 | 1.1 |  | 9.591 | 13.9686 | 0.44661
AA-90 | 6.7 | 1096.1 | 138 | 5 | 0.58394 | 986.6153 | 36.92 | 983.2578 |  |  |  | 995.5935 | 56 | 1.1 |  | 8.9782 | 13.3847 | 0.44661
AA-91 | 8 | 1104.1 | 95 | 7.5 | 1.0442 | 987.6595 | 36.92 | 991.1893 |  |  |  | 995.559 | 56 | 1.1 |  | 7.8995 | 12.3405 | 0.44661
AA-92 | 14 | 1118.1 | 90 | -7 | -1.7062 | 985.9533 | 40.0458 | 1004.7288 |  |  |  | 995.4986 | 56 | 1.1 |  | 9.5453 | 14.0467 | 0.44661
AA-93 | 15 | 1133.1 | 77 | -2 | -0.52349 | 985.4298 | 40.569 | 1019.7106 |  |  |  | 995.434 | 56 | 1.1 |  | 10.0041 | 14.5702 | 0.44661
AA-94 | 10 | 1143.1 | 88 | -7.5 | -1.3053 | 984.1246 | 41.9488 | 1029.5285 |  |  |  | 995.3909 | 56 | 1.1 |  | 11.2663 | 15.8754 | 0.44661
AA-95 | 21 | 1164.1 | 82 | 6 | 2.1951 | 986.3197 | 47.0014 | 1049.7931 |  |  |  | 995.3003 | 56 | 1.1 |  | 8.9807 | 13.6803 | 0.44661
AA-96 | 12.2 | 1176.3 | 76 | 1 | 0.21292 | 986.5326 | 55.6268 | 1058.4185 |  |  |  | 995.2477 | 56 | 1.1 |  | 8.7151 | 13.4674 | 0.44661
AA-97 | 16 | 1192.3 | 45 | -7 | -1.9499 | 984.5827 | 52.325 | 1073.9522 |  |  |  | 995.1788 | 56 | 1.1 |  | 10.5961 | 15.4173 | 0.44661
AA-98 | 9 | 1201.3 | 102 | -3 | -0.47102 | 984.1117 | 45.8598 | 1080.1956 |  |  |  | 995.14 | 56 | 1.1 |  | 11.0283 | 15.8883 | 0.44661
AA-99 | 15 | 1216.3 | 136 | -1 | -0.26179 | 983.8499 | 34.3709 | 1089.8359 |  |  |  | 995.0753 | 56 | 1.1 |  | 11.2254 | 16.1501 | 0.44661
AA-100 | 14 | 1230.3 | 140 | 7 | 1.7062 | 985.5561 | 21.1553 | 1094.1299 |  |  | rocas fin de dia | 995.015 | 56 | 1.1 |  | 9.4589 | 14.4439 | 0.44661
AA-101 | 15 | 1245.3 | 162 | 4.5 | 1.1769 | 986.7329 | 26.9982 | 1107.8949 |  |  |  | 994.9503 | 56 | 1.1 |  | 8.2174 | 13.2671 | 0.44661
AA-102 | 6 | 1251.3 | 67 | -17.5 | -1.8042 | 984.9287 | 26.5991 | 1113.6033 |  |  |  | 994.9244 | 56 | 1.1 |  | 9.9957 | 15.0713 | 0.44661
AA-103 | 17 | 1268.3 | 94 | 11 | 3.2438 | 988.1725 | 27.7631 | 1130.2503 |  |  | 12 m HG | 994.8512 | 56 | 1.1 |  | 6.6787 | 11.8275 | 0.44661
AA-104 | 11.9 | 1280.2 | 86 | 5 | 1.0372 | 989.2096 | 33.6905 | 1140.5168 |  |  | 6m HG | 994.7999 | 56 | 1.1 |  | 5.5902 | 10.7904 | 0.44661
AA-105 | 10 | 1290.2 | 60 | -0.5 | -0.087265 | 989.1223 | 36.1096 | 1150.2194 |  |  |  | 994.7567 | 56 | 1.1 |  | 5.6344 | 10.8777 | 0.44661
AA-106 | 11 | 1301.2 | 76 | -15.5 | -2.9396 | 986.1827 | 38.674 | 1160.5044 |  |  |  | 994.7093 | 56 | 1.1 |  | 8.5266 | 13.8173 | 0.44661
AA-107 | 15 | 1316.2 | 76 | 10.5 | 2.7335 | 988.9163 | 40.2156 | 1175.1725 |  |  | 6m HG (roca grande) | 994.6447 | 56 | 1.1 |  | 5.7284 | 11.0837 | 0.44661
AA-108 | 20 | 1336.2 | 84 | -6.5 | -2.2641 | 986.6522 | 40.2156 | 1195.0439 |  |  |  | 994.5585 | 56 | 1.1 |  | 7.9063 | 13.3478 | 0.44661
AA-109 | 12.5 | 1348.7 | 90 | 11 | 2.3851 | 989.0373 | 41.4982 | 1207.247 |  |  |  | 994.5046 | 56 | 1.1 |  | 5.4673 | 10.9627 | 0.44661
AA-110 | 16 | 1364.7 | 84 | -14 | -3.8708 | 985.1666 | 43.121 | 1222.6867 |  |  |  | 994.4356 | 56 | 1.1 |  | 9.269 | 14.8334 | 0.44661
AA-111 | 17 | 1381.7 | 84 | -14 | -4.1127 | 981.0539 | 43.121 | 1239.1817 |  |  |  | 994.3623 | 56 | 1.1 |  | 13.3084 | 18.9461 | 0.44661
AA-112 | 20 | 1401.7 | 90 | 1 | 0.34905 | 981.4029 | 39.6486 | 1258.8749 |  |  |  | 994.2761 | 56 | 1.1 |  | 12.8732 | 18.5971 | 0.44661
AA-113 | 15 | 1416.7 | 100 | -2 | -0.52349 | 980.8794 | 39.1254 | 1273.8566 |  |  | rocas 12m HG/ construir puente | 994.2114 | 56 | 1.1 |  | 13.332 | 19.1206 | 0.44661
AA-114 | 11 | 1427.7 | 92 | 15 | 2.847 | 983.7264 | 45.9551 | 1281.996 |  |  |  | 994.164 | 56 | 1.1 |  | 10.4376 | 8.6403 | 0.44661
AA-115 | 15.5 | 1443.2 | 50 | -9 | -2.4247 | 981.3017 | 55.7957 | 1293.7235 |  |  |  | 994.0972 | 56 | 1.1 |  | 12.7955 | 11.065 | 0.44661
AA-116 | 14 | 1457.2 | 50 | -6 | -1.4634 | 979.8383 | 64.7454 | 1304.3894 |  |  |  | 994.0368 | 56 | 1.1 |  | 14.1985 | 12.5284 | 0.44661
AA-117 | 17 | 1474.2 | 50 | -4 | -1.1859 | 978.6525 | 76.737 | 1316.3809 |  |  |  | 993.9636 | 56 | 1.1 |  | 15.3111 | 13.7143 | 0.44661
AA-118 | 20 | 1494.2 | 45 | -9.5 | -3.301 | 975.3515 | 86.5998 | 1333.4639 |  |  |  | 993.8773 | 56 | 1.1 |  | 18.5258 | 17.0153 | 0.44661
AA-119 | 15 | 1509.2 | 60 | 7.5 | 1.9579 | 977.3094 | 95.7557 | 1345.1829 |  |  | alongside big rock | 993.8127 | 56 | 1.1 |  | 16.5033 | 15.0574 | 0.44661
AA-120 | 14 | 1523.2 | 52 | -18 | -4.3262 | 972.9832 | 100.3096 | 1357.6947 |  |  |  | 993.7523 | 56 | 1.1 |  | 20.7692 | 19.3836 | 0.44661
AA-121 | 17 | 1540.2 | 70 | -2 | -0.59329 | 972.3899 | 108.2858 | 1372.6957 |  |  |  | 993.679 | 56 | 1.1 |  | 21.2892 | 19.9769 | 0.44661
AA-122 | 17 | 1557.2 | 62 | -1 | -0.29669 | 972.0932 | 114.0993 | 1388.668 |  |  |  | 993.6058 | 56 | 1.1 |  | 21.5126 | 20.2736 | 0.44661
AA-123 | 21 | 1578.2 | 70 | -5 | -1.8303 | 970.2629 | 124.5593 | 1406.7853 |  |  |  | 993.5152 | 56 | 1.1 |  | 23.2523 | 22.1039 | 0.44661
AA-124 | 17 | 1595.2 | 60 | -1 | -0.29669 | 969.9662 | 127.5109 | 1423.5245 |  |  |  | 993.442 | 56 | 1.1 |  | 23.4757 | 22.4005 | 0.44661
AA-125 | 19 | 1614.2 | 80 | -6 | -1.986 | 967.9802 | 130.7921 | 1442.1334 |  |  |  | 993.36 | 56 | 1.1 |  | 25.3799 | 24.3866 | 0.44661
AA-126 | 18 | 1632.2 | 80 | 6 | 1.8815 | 969.8617 | 133.9007 | 1459.7628 |  |  |  | 993.2825 | 56 | 1.1 |  | 23.4208 | 22.5051 | 0.44661
AA-127 | 14 | 1646.2 | 80 | -4 | -0.97659 | 968.8851 | 136.3258 | 1473.5165 |  |  |  | 993.2221 | 56 | 1.1 |  | 24.337 | 23.4817 | 0.44661
AA-128 | 10 | 1656.2 | 80 | 2 | 0.34899 | 969.2341 | 137.023 | 1483.4861 |  |  |  | 993.179 | 56 | 1.1 |  | 23.9449 | 23.1327 | 0.44661
AA-129 | 16 | 1672.2 | 86 | -10 | -2.7784 | 966.4557 | 134.2868 | 1499.0036 |  |  |  | 993.11 | 56 | 1.1 |  | 26.6543 | 25.911 | 0.44661
AA-130 | 17 | 1689.2 | 100 | 5.5 | 1.6294 | 968.0851 | 131.3484 | 1515.6683 |  |  |  | 993.0367 | 56 | 1.1 |  | 24.9516 | 24.2817 | 0.44661
AA-131 | 16 | 1705.2 | 100 | 12 | 3.3266 | 971.4117 | 131.3484 | 1531.3187 |  |  |  | 992.9678 | 56 | 1.1 |  | 21.5561 | 20.9551 | 0.44661
AA-132 | 13 | 1718.2 | 90 | 1 | 0.22688 | 971.6386 | 131.802 | 1544.3088 |  |  |  | 992.9117 | 56 | 1.1 |  | 21.2732 | 20.7282 | 0.44661
AA-133 | 16 | 1734.2 | 88 | 4 | 1.1161 | 972.7547 | 131.802 | 1560.2698 |  |  | dense tree clumps | 992.8428 | 56 | 1.1 |  | 20.0881 | 19.6121 | 0.44661
AA-134 | 16.8 | 1751 | 90 | 5 | 1.4642 | 974.2189 | 134.7082 | 1576.7516 |  |  |  | 992.7703 | 56 | 1.1 |  | 18.5514 | 18.1479 | 0.44661
AA-135 | 15 | 1766 | 80 | 3.5 | 0.91573 | 975.1346 | 134.7082 | 1591.7236 |  |  |  | 992.7057 | 56 | 1.1 |  | 17.5711 | 17.2321 | 0.44661
AA-136 | 18 | 1784 | 90 | 2 | 0.62819 | 975.7628 | 128.5556 | 1608.6278 |  |  |  | 992.6281 | 56 | 1.1 |  | 16.8653 | 16.604 | 0.44661
AA-137 | 14 | 1798 | 110 | 11 | 2.6713 | 978.4341 | 127.5969 | 1622.3371 |  |  | arbol chilup | 992.5677 | 56 | 1.1 |  | 14.1336 | 13.9326 | 0.44661
AA-138 | 13 | 1811 | 94 | 3.5 | 0.79363 | 979.2278 | 126.2406 | 1635.2418 |  |  |  | 992.5117 | 56 | 1.1 |  | 13.2839 | 13.139 | 0.44661
AA-139 | 15.5 | 1826.5 | 96 | 1 | 0.27051 | 979.4983 | 128.9317 | 1650.5039 |  |  |  | 992.4449 | 56 | 1.1 |  | 12.9466 | 12.8685 | 0.44661
AA-140 | 15 | 1841.5 | 80 | 3 | 0.78504 | 980.2833 | 131.5329 | 1665.2558 |  |  |  | 992.3802 | 56 | 1.1 |  | 12.0969 | 12.0834 | 0.44661
AA-141 | 17.7 | 1859.2 | 80 | 1.5 | 0.46333 | 980.7466 | 131.5329 | 1682.9498 |  |  |  | 992.3039 | 56 | 1.1 |  | 11.5573 | 11.6201 | 0.44661
AA-142 | 17 | 1876.2 | 90 | 1.5 | 0.44501 | 981.1917 | 134.4839 | 1699.6857 |  |  |  | 992.2306 | 56 | 1.1 |  | 11.039 | 11.1751 | 0.44661
AA-143 | 19 | 1895.2 | 80 | 2.5 | 0.82877 | 982.0204 | 140.9761 | 1717.5229 |  |  |  | 992.1487 | 56 | 1.1 |  | 10.1283 | 10.3463 | 0.44661
AA-144 | 18 | 1913.2 | 70 | -3 | -0.94205 | 981.0784 | 146.5308 | 1734.6185 |  |  |  | 992.0711 | 56 | 1.1 |  | 10.9927 | 11.2884 | 0.44661
AA-145 | 16 | 1929.2 | 72 | -4.5 | -1.2553 | 979.823 | 149.3006 | 1750.3268 |  |  |  | 992.0021 | 56 | 1.1 |  | 12.1791 | 12.5437 | 0.44661
AA-146 | 16 | 1945.2 | 80 | -3 | -0.83738 | 978.9857 | 152.0751 | 1766.0621 |  |  |  | 991.9332 | 56 | 1.1 |  | 12.9475 | 13.3811 | 0.44661
AA-147 | 14 | 1959.2 | 80 | 7 | 1.7062 | 980.6918 | 151.1058 | 1779.9239 |  |  |  | 991.8728 | 56 | 1.1 |  | 11.181 | 11.6749 | 0.44661
AA-148 | 13 | 1972.2 | 94 | 1 | 0.22688 | 980.9187 | 148.8487 | 1792.7245 |  |  |  | 991.8168 | 56 | 1.1 |  | 10.8981 | 11.4481 | 0.44661
AA-149 | 13 | 1985.2 | 100 | 3 | 0.68037 | 981.5991 | 144.4086 | 1804.9238 |  |  | 2 45* codos | 991.7607 | 56 | 1.1 |  | 10.1617 | 10.7677 | 0.44661
AA-150 | 13 | 1998.2 | 110 | 8 | 1.8093 | 983.4083 | 137.9718 | 1816.0725 |  |  | 6m HG | 991.7047 | 56 | 1.1 |  | 8.2964 | 8.9584 | 0.44661
AA-151 | 12 | 2010.2 | 120 | 12 | 2.4949 | 985.9033 | 141.9864 | 1827.1024 |  |  |  | 991.653 | 56 | 1.1 |  | 5.7497 | 6.4635 | 0.44661
AA-152 | 14 | 2024.2 | 70 | -10.5 | -2.5513 | 983.352 | 148.8692 | 1839.0238 |  |  |  | 991.5926 | 56 | 1.1 |  | 8.2407 | 9.0148 | 0.44661
AA-153 | 9 | 2033.2 | 60 | -19 | -2.9301 | 980.4219 | 153.7501 | 1845.9945 |  |  | 12m HG | 991.5538 | 56 | 1.1 |  | 11.132 | 11.9449 | 0.44661
AA-154 | 14 | 2047.2 | 55 | -11.5 | -2.7912 | 977.6307 | 158.4423 | 1858.8861 |  |  | muchas rocas | 991.4935 | 56 | 1.1 |  | 13.8628 | 14.7361 | 0.44661
AA-155 | 15 | 2062.2 | 70 | -0.5 | -0.1309 | 977.4998 | 162.071 | 1873.4399 |  |  |  | 991.4288 | 56 | 1.1 |  | 13.929 | 14.867 | 0.44661
AA-156 | 15 | 2077.2 | 76 | -4 | -1.0463 | 976.4535 | 164.6693 | 1888.1761 |  |  | 3 trees de chilup | 991.3641 | 56 | 1.1 |  | 14.9107 | 15.9133 | 0.44661
AA-157 | 15 | 2092.2 | 80 | -1 | -0.26179 | 976.1917 | 167.2737 | 1902.9459 |  |  |  | 991.2995 | 56 | 1.1 |  | 15.1078 | 16.1751 | 0.44661
AA-158 | 18 | 2110.2 | 80 | -4 | -1.2556 | 974.9361 | 167.2737 | 1920.9021 |  |  |  | 991.2219 | 56 | 1.1 |  | 16.2858 | 17.4307 | 0.44661
AA-159 | 15 | 2125.2 | 90 | -1 | -0.26179 | 974.6743 | 169.878 | 1935.672 |  |  |  | 991.1572 | 56 | 1.1 |  | 16.483 | 17.6925 | 0.44661
AA-160 | 13 | 2138.2 | 80 | 7 | 1.5843 | 976.2586 | 174.2911 | 1947.7969 |  |  |  | 991.1012 | 56 | 1.1 |  | 14.8426 | 16.1082 | 0.44661
AA-161 | 19 | 2157.2 | 70 | 0 | 0 | 976.2586 | 172.3051 | 1966.6928 |  |  |  | 991.0193 | 56 | 1.1 |  | 14.7607 | 16.1082 | 0.44661
AA-162 | 17 | 2174.2 | 96 | 4.5 | 1.3338 | 977.5924 | 170.5336 | 1983.5476 |  |  |  | 990.946 | 56 | 1.1 |  | 13.3536 | 14.7744 | 0.44661
AA-163 | 17 | 2191.2 | 96 | 5 | 1.4816 | 979.074 | 169.9425 | 2000.4726 |  |  |  | 990.8727 | 56 | 1.1 |  | 11.7987 | 13.2927 | 0.44661
AA-164 | 14 | 2205.2 | 92 | 2.5 | 0.61067 | 979.6847 | 171.4045 | 2014.3826 |  |  |  | 990.8124 | 56 | 1.1 |  | 11.1277 | 12.6821 | 0.44661
AA-165 | 14.5 | 2219.7 | 84 | -1 | -0.25306 | 979.4316 | 176.3631 | 2028.0061 |  |  |  | 990.7499 | 56 | 1.1 |  | 11.3182 | 12.9351 | 0.44661
AA-166 | 12 | 2231.7 | 70 | -6 | -1.2543 | 978.1773 | 181.9659 | 2038.5434 |  |  |  | 990.6981 | 56 | 1.1 |  | 12.5208 | 14.1895 | 0.44661
AA-167 | 24 | 2255.7 | 62 | -1 | -0.41886 | 977.7584 | 190.1731 | 2061.0926 |  |  |  | 990.5947 | 56 | 1.1 |  | 12.8362 | 14.6083 | 0.44661
AA-168 | 14 | 2269.7 | 70 | 4 | 0.97659 | 978.735 | 190.1731 | 2075.0585 |  |  |  | 990.5343 | 56 | 1.1 |  | 11.7993 | 13.6317 | 0.44661
AA-169 | 13 | 2282.7 | 90 | -1.5 | 0.68037 | 979.4154 | 190.1731 | 2088.054 |  |  |  | 990.4783 | 56 | 1.1 |  | 11.0629 | 12.9514 | 0.44661
AA-170 | 25 | 2307.7 | 90 | 3 | 2.1789 | 981.5943 | 181.6343 | 2111.5142 |  |  |  | 990.3705 | 56 | 1.1 |  | 8.7762 | 10.7725 | 0.44661
AA-171 | 25 | 2332.7 | 110 | 5 | 1.5262 | 983.1205 | 177.3096 | 2136.0407 |  |  |  | 990.2627 | 56 | 1.1 |  | 7.1422 | 9.2463 | 0.44661
AA-172 | 15 | 2347.7 | 100 | 3.5 | -1.0463 | 982.0742 | 188.7789 | 2145.6645 |  |  |  | 990.1981 | 56 | 1.1 |  | 8.1239 | 10.2926 | 0.44661
AA-173 | 20 | 2367.7 | 40 | -4 | -1.3951 | 980.679 | 202.8865 | 2159.7722 |  |  |  | 990.1119 | 56 | 1.1 |  | 9.4328 | 11.6877 | 0.44661
AA-174 | 18 | 2385.7 | 45 | -4 | -0.94205 | 979.737 | 216.6418 | 2171.3142 |  |  |  | 990.0343 | 56 | 1.1 |  | 10.2973 | 12.6298 | 0.44661
AA-175 | 12 | 2397.7 | 40 | -3 | 1.8772 | 981.6142 | 224.3446 | 2180.4941 |  |  | milpas | 989.9825 | 56 | 1.1 |  | 8.3683 | 10.7526 | 0.44661
AA-176 | 8 | 2405.7 | 50 | 9 | -1.2515 | 980.3627 | 229.4236 | 2186.547 |  |  | milpas | 989.948 | 56 | 1.1 |  | 9.5853 | 12.004 | 0.44661
AA-177 | 15 | 2420.7 | 50 | -9 | -1.3073 | 979.0554 | 239.7152 | 2197.2043 |  |  | milpas | 989.8834 | 56 | 1.1 |  | 10.828 | 13.3114 | 0.44661
AA-178 | 11 | 2431.7 | 46 | -5 | -0.38389 | 978.6715 | 249.0082 | 2203.0112 |  |  | milpas | 989.6072 | 39 | 1.1 |  | 10.9358 | 13.6953 | 0.44661
AA-179 | 18 | 2449.7 | 32 | -2 | -0.31414 | 978.3573 | 266.1168 | 2197.4523 |  |  | fin de milpas | 989.1554 | 39 | 1.1 |  | 10.798 | 14.0094 | 0.92082
AA-180 | 26 | 2475.7 | 342 | -1 | -1.8137 | 976.5437 | 290.5451 | 2188.5611 |  |  | Start of Day | 988.5026 | 39 | 1.1 |  | 11.959 | 15.8231 | 0.92082
AA-181 | 18 | 2493.7 | 340 | -4 | 0 | 976.5437 | 302.0871 | 2174.8059 |  |  | rocas | 988.0508 | 39 | 1.1 |  | 11.5071 | 15.8231 | 0.92082
AA-182 | 11 | 2504.7 | 310 | 0 | -0.95871 | 975.585 | 309.1578 | 2166.3794 |  |  |  | 987.7746 | 39 | 1.1 |  | 12.1897 | 16.7818 | 0.92082
AA-183 | 20 | 2524.7 | 310 | -5 | -1.9169 | 973.668 | 321.9646 | 2151.1168 |  |  | 6m HG | 987.2725 | 39 | 1.1 |  | 13.6045 | 18.6987 | 0.92082
AA-184 | 21 | 2545.7 | 310 | -5.5 | -1.4649 | 972.2032 | 335.401 | 2135.104 |  |  |  | 986.7453 | 39 | 1.1 |  | 14.5422 | 20.1636 | 0.92082
AA-185 | 20 | 2565.7 | 310 | -4 | -1.7431 | 970.46 | 350.6846 | 2122.2795 |  |  |  | 986.2432 | 39 | 1.1 |  | 15.7832 | 21.9067 | 0.92082
AA-186 | 22 | 2587.7 | 320 | -5 | -0.57589 | 969.8841 | 369.6646 | 2111.3214 |  |  |  | 985.691 | 39 | 1.1 |  | 15.8068 | 22.4826 | 0.92082
AA-187 | 29 | 2616.7 | 330 | -1.5 | 0 | 969.8841 | 394.7708 | 2096.8264 |  |  |  | 984.9629 | 39 | 1.1 |  | 15.0788 | 22.4826 | 0.92082
AA-188 | 29 | 2645.7 | 330 | 0 | -2.5275 | 967.3566 | 416.9861 | 2078.1855 |  |  |  | 984.2349 | 39 | 1.1 |  | 16.8783 | 25.0101 | 0.92082
AA-189 | 15 | 2660.7 | 320 | -5 | -2.0876 | 965.269 | 426.5912 | 2066.7386 |  |  |  | 983.8583 | 39 | 1.1 |  | 18.5893 | 27.0977 | 0.92082
AA-190 | 26 | 2686.7 | 310 | -8 | -2.266 | 963.003 | 443.141 | 2047.0152 |  |  |  | 983.2056 | 39 | 1.1 |  | 20.2026 | 29.3638 | 0.92082
AA-191 | 27 | 2713.7 | 310 | -5 | -2.8223 | 960.1807 | 460.4302 | 2026.4108 |  |  | arboles de pino | 982.5278 | 39 | 1.1 |  | 22.3471 | 32.186 | 0.92082
AA-192 | 19 | 2732.7 | 310 | -6 | -1.3254 | 958.8553 | 472.5763 | 2011.9356 |  |  |  | 982.0508 | 39 | 1.1 |  | 23.1955 | 33.5114 | 0.92082
AA-193 | 15 | 2747.7 | 310 | -4 | -1.0463 | 957.809 | 486.6373 | 2006.8178 |  |  |  | 981.6743 | 39 | 1.1 |  | 23.8653 | 34.5578 | 0.92082
AA-194 | 61 | 2808.7 | 340 | -4 | -1.0646 | 956.7444 | 543.819 | 1986.0054 |  |  | milpas | 980.1429 | 39 | 1.1 |  | 23.3985 | 35.6224 | 0.92082
AA-195 | 36 | 2844.7 | 340 | -1 | -1.5703 | 955.1741 | 578.587 | 1976.6894 |  |  | milpas | 979.2391 | 39 | 1.1 |  | 24.065 | 37.1927 | 0.92082
AA-196 | 24 | 2868.7 | 345 | -2.5 | 0 | 955.1741 | 601.1182 | 1968.4887 |  |  |  | 978.9043 | 44 | 1.1 |  | 23.7302 | 37.1927 | 0.92082
AA-197 | 28 | 2896.7 | 340 | 0 | 0.24434 | 955.4184 | 629.1182 | 1968.4887 |  |  |  | 978.5137 | 44 | 1.1 |  | 23.0952 | 36.9483 | 0.72343
AA-198 | 27 | 2923.7 | 0 | 0.5 | 0.47121 | 955.8897 | 655.707 | 1968.4887 |  |  | bosque | 978.137 | 44 | 1.1 |  | 22.2473 | 36.4771 | 0.72343
AA-199 | 16 | 2939.7 | 350 | 1 | -0.55839 | 955.3313 | 671.4615 | 1965.712 |  |  |  | 977.9137 | 44 | 1.1 |  | 22.5825 | 37.0355 | 0.72343
AA-200 | 21 | 2960.7 | 350 | -2 | 0 | 955.3313 | 692.3688 | 1962.0654 |  |  |  | 977.6208 | 44 | 1.1 |  | 22.2895 | 37.0355 | 0.72343
AA-201 | 22.5 | 2983.2 | 355 | 0 | -1.3736 | 953.9577 | 713.5119 | 1960.1081 |  |  |  | 977.3068 | 44 | 1.1 |  | 23.3492 | 38.4091 | 0.72343
AA-202 | 13 | 2996.2 | 340 | -3.5 | -0.45369 | 953.504 | 725.2719 | 1955.6645 |  |  |  | 977.1255 | 44 | 1.1 |  | 23.6215 | 38.8628 | 0.72343
AA-203 | 27 | 3023.2 | 335 | -2 | 0.94229 | 954.4463 | 750.6282 | 1944.2608 |  |  |  | 976.7488 | 44 | 1.1 |  | 22.3025 | 37.9205 | 0.72343
AA-204 | 15 | 3038.2 | 340 | 2 | 1.5679 | 956.0142 | 765.3913 | 1939.1586 |  |  |  | 976.5395 | 44 | 1.1 |  | 20.5253 | 36.3526 | 0.72343
AA-205 | 33 | 3071.2 | 350 | 6 | 0.86384 | 956.878 | 797.7119 | 1933.4301 |  |  |  | 976.0791 | 44 | 1.1 |  | 19.2011 | 35.4887 | 0.72343
AA-206 | 12 | 3083.2 | 350 | 1.5 | -4.3004 | 952.5776 | 808.1007 | 1931.4848 |  |  |  | 975.9117 | 44 | 1.1 |  | 23.3341 | 39.7891 | 0.72343
AA-207 | 37 | 3120.2 | 330 | -21 | -12.6547 | 939.9229 | 834.5617 | 1914.1004 |  |  | fin de bosque Tanque de distribucion | 939.9229 | 39 | 1.1 |  | 0 | 0 | 0.72343
B-01 | 29 | 3149.2 | 40 | -20 | -6.0294 | 933.8934 | 858.1619 | 1932.3339 |  |  | CASA 1 (15m, 320*, futuro) | 937.707 | 23 | 0.5 |  | 3.8136 | 6.0294 | 0.92082
B-02 | 16 | 3165.2 | 30 | -12 | -3.7351 | 930.1583 | 871.1366 | 1940.1129 |  |  |  | 936.4845 | 23 | 0.5 |  | 6.3262 | 9.7646 | 1.2034
B-03 | 12 | 3177.2 | 34 | -13.5 | -3.1058 | 927.0525 | 880.0751 | 1946.5946 |  |  |  | 935.5676 | 23 | 0.5 |  | 8.5151 | 12.8704 | 1.2034
B-04 | 9 | 3186.2 | 40 | -15 | -1.6401 | 925.4124 | 888.2442 | 1952.2828 |  |  |  | 934.88 | 23 | 0.5 |  | 9.4676 | 14.5105 | 1.2034
B-05 | 7 | 3193.2 | 20 | -10.5 | -1.2756 | 924.1367 | 893.0254 | 1954.5465 |  |  | CASA 2 (120m, 340*) | 934.3451 | 23 | 0.5 |  | 10.2084 | 15.7862 | 1.2034
B-06 | 9 | 3202.2 | 46 | -19 | -2.9301 | 921.2066 | 898.9367 | 1960.7377 |  |  |  | 933.6574 | 23 | 0.5 |  | 12.4508 | 18.7163 | 1.2034
B-07 | 10 | 3212.2 | 46 | -17 | -2.9237 | 918.2829 | 905.0837 | 1967.5593 |  |  |  | 932.8934 | 23 | 0.5 |  | 14.6105 | 21.64 | 1.2034
B-08 | 12.5 | 3224.7 | 50 | -18.5 | -3.9663 | 914.3166 | 912.7033 | 1976.6132 |  |  |  | 931.9383 | 23 | 0.5 |  | 17.6217 | 25.6063 | 1.2034
B-09 | 15.7 | 3240.4 | 50 | -19 | -5.1114 | 909.2052 | 920.1257 | 1987.9148 |  |  |  | 930.7387 | 23 | 0.5 |  | 21.5335 | 30.7177 | 1.2034
B-10 | 12 | 3252.4 | 60 | -20 | -4.1042 | 905.1009 | 925.7638 | 1997.853 |  |  |  | 929.8218 | 23 | 0.5 |  | 24.7209 | 34.822 | 1.2034
B-11 | 12 | 3264.4 | 60 | -17 | -3.5085 | 901.5925 | 931.5016 | 2007.7367 |  |  |  | 928.9049 | 23 | 0.5 |  | 27.3124 | 38.3304 | 1.2034
B-12 | 11 | 3275.4 | 60 | -18 | -3.3992 | 898.1933 | 935.7568 | 2016.7439 |  |  |  | 928.0644 | 23 | 0.5 |  | 29.8711 | 41.7296 | 1.2034
B-13 | 12 | 3287.4 | 66 | -19 | -3.9068 | 894.2864 | 940.3717 | 2026.9784 |  |  |  | 927.1475 | 23 | 0.5 |  | 32.861 | 45.6364 | 1.2034
B-14 | 10 | 3297.4 | 66 | -21 | -3.5837 | 890.7028 | 945.0396 | 2035.324 |  |  |  | 926.3834 | 23 | 0.5 |  | 35.6806 | 49.2201 | 1.2034
B-15 | 12 | 3309.4 | 60 | -24 | -4.8808 | 885.8219 | 950.5209 | 2045.0261 |  |  |  | 925.4665 | 23 | 0.5 |  | 39.6446 | 54.1009 | 1.2034
B-16 | 11 | 3320.4 | 60 | -21 | -3.942 | 881.8799 | 955.6556 | 2054.523 |  |  |  | 924.626 | 23 | 0.5 |  | 42.7462 | 58.043 | 1.2034
B-17 | 10 | 3330.4 | 60 | -4.5 | -0.78459 | 881.0953 | 960.6402 | 2063.0517 |  |  |  | 923.862 | 23 | 0.5 |  | 42.7667 | 58.8276 | 1.2034
B-18 | 10 | 3340.4 | 60 | -10 | -1.7365 | 879.3588 | 965.5642 | 2071.3553 |  |  |  | 923.0979 | 23 | 0.5 |  | 43.7391 | 60.5641 | 1.2034
B-19 | 12 | 3352.4 | 60 | -16.5 | -3.4082 | 875.9506 | 971.3171 | 2081.6465 |  |  |  | 922.181 | 23 | 0.5 |  | 46.2304 | 63.9723 | 1.2034
B-20 | 11 | 3363.4 | 60 | -8 | -1.5309 | 874.4197 | 976.7636 | 2091.1365 |  |  |  | 921.3405 | 23 | 0.5 |  | 46.9208 | 65.5032 | 1.2034
B-21 | 14 | 3377.4 | 60 | -5 | -1.2202 | 873.1995 | 983.7369 | 2103.2493 |  |  |  | 920.2708 | 23 | 0.5 |  | 47.0713 | 66.7233 | 1.2034
B-22 | 15 | 3392.4 | 60 | -2.5 | -0.65429 | 872.5452 | 990.7723 | 2116.2219 |  |  |  | 919.1247 | 23 | 0.5 |  | 46.5794 | 67.3776 | 1.2034
B-23 | 14 | 3406.4 | 62 | 3 | 0.7327 | 873.278 | 996.9011 | 2128.5154 |  |  | CASA 3 (10m, 340*) | 918.055 | 23 | 0.5 |  | 44.777 | 66.6449 | 1.2034
B-24 | 15 | 3421.4 | 64 | 6 | 1.5679 | 874.8459 | 1004.36 | 2141.9645 |  |  |  | 916.9089 | 23 | 0.5 |  | 42.063 | 65.077 | 1.2034
B-25 | 8 | 3429.4 | 60 | 4 | 0.55805 | 875.4039 | 1011.8592 | 2148.8885 |  |  |  | 916.2976 | 23 | 0.5 |  | 40.8937 | 64.5189 | 1.2034
B-26 | 28 | 3457.4 | 20 | -2 | -0.97719 | 874.4267 | 1038.1546 | 2158.3047 |  |  | arbol de aguacate (B26-C1)/ (B26-D1) | 914.1582 | 23 | 0.5 |  | 39.7314 | 65.4961 | 1.2034
B-27 | 21 | 3478.4 | 20 | -10.5 | -3.8269 | 870.5998 | 1057.0178 | 2165.1159 |  |  |  | 912.5536 | 23 | 0.5 |  | 41.9538 | 69.3231 | 1.2034
B-28 | 23 | 3501.4 | 24 | -18.5 | -7.298 | 863.3018 | 1076.9436 | 2173.7272 |  |  |  | 910.7962 | 23 | 0.5 |  | 47.4944 | 76.6211 | 1.2034
B-29 | 24 | 3525.4 | 24 | -23 | -9.3775 | 853.9242 | 1097.1257 | 2182.8405 |  |  |  | 908.9624 | 23 | 0.5 |  | 55.0382 | 85.9986 | 1.2034
B-30 | 20 | 3545.4 | 24 | -21 | -7.1674 | 846.7569 | 1113.9077 | 2190.2131 |  |  |  | 907.4343 | 23 | 0.5 |  | 60.6774 | 93.166 | 1.2034
B-31 | 25.5 | 3570.9 | 26 | -25 | -10.7768 | 835.9801 | 1134.6795 | 2201.0595 |  |  |  | 905.4859 | 23 | 0.5 |  | 69.5058 | 103.9428 | 1.2034
B-32 | 71 | 3641.9 | 26 | -14 | -17.1765 | 818.8037 | 1194.3409 | 2232.108 |  |  | pequeño bosque | 900.0609 | 23 | 0.5 |  | 81.2573 | 121.1192 | 1.2034
B-33 | 23 | 3664.9 | 30 | 4 | 1.6044 | 820.4081 | 1214.211 | 2243.5726 |  |  |  | 898.3036 | 23 | 0.5 |  | 77.8955 | 119.5148 | 1.2034
B-34 | 29 | 3693.9 | 30 | 4.5 | 2.2753 | 822.6834 | 1239.2483 | 2258.0704 |  |  |  | 896.0877 | 23 | 0.5 |  | 73.4044 | 117.2395 | 1.2034
B-35 | 55 | 3748.9 | 30 | 1 | 0.95988 | 823.6433 | 1261.6154 | 2285.2318 |  |  | CASA 7, cementerio | 891.8853 | 23 | 0.5 |  | 68.242 | 116.2796 | 1.2034
B-36 | 56 | 3804.9 | 66 | -9 | -8.7603 | 814.8829 | 1271.22 | 2336.3592 |  |  | CASA 4 (20m 190*), CASA 5(20m 300*), CASA 6 (20m 350*) | 887.6065 | 23 | 0.5 |  | 72.7235 | 125.0399 | 1.2034
B-37 | 52 | 3856.9 | 80 | -2 | -1.8148 | 813.0682 | 1273.0336 | 2387.5517 |  |  | CASA 8 (10m 192*), CASA 9 (10m 0*), CASA 10(50m 340*) | 883.6333 | 23 | 0.5 |  | 70.5651 | 126.8547 | 1.2034
B-38 | 19 | 3875.9 | 88 | -1.5 | -0.49736 | 812.5708 | 1276.9826 | 2406.4678 |  |  | CASA 11(120m 340*) | 882.1815 | 23 | 0.5 |  | 69.6107 | 127.3521 | 1.2034
B-39 | 23 | 3898.9 | 78 | -5 | -2.0046 | 810.5662 | 1294.0099 | 2428.9515 |  |  |  | 880.4241 | 23 | 0.5 |  | 69.8579 | 129.3567 | 1.2034
B-40 | 17.5 | 3916.4 | 42 | 2 | 0.61074 | 811.177 | 1305.2518 | 2440.6395 |  |  | bosque | 879.087 | 23 | 0.5 |  | 67.91 | 128.7459 | 1.2034
B-41 | 13 | 3929.4 | 50 | -3.5 | -0.79363 | 810.3833 | 1315.1918 | 2450.5601 |  |  |  | 878.0937 | 23 | 0.5 |  | 67.7104 | 129.5396 | 1.2034
B-42 | 19 | 3948.4 | 40 | -5 | -1.656 | 808.7274 | 1331.5837 | 2462.5876 |  |  |  | 876.6419 | 23 | 0.5 |  | 67.9146 | 131.1955 | 1.2034
B-43 | 17 | 3965.4 | 30 | -10 | -2.952 | 805.7753 | 1347.3158 | 2471.0552 |  |  | CASA 12 (15m 120*), CASA 13 and 14(30m 120*) | 875.343 | 23 | 0.5 |  | 69.5677 | 134.1475 | 1.2034
B-44 | 16 | 3981.4 | 20 | -5 | -1.3945 | 804.3809 | 1359.5258 | 2476.52 |  |  |  | 874.1205 | 23 | 0.5 |  | 69.7396 | 135.542 | 1.2034
B-45 | 28 | 4009.4 | 40 | -3 | -1.4654 | 802.9154 | 1380.9457 | 2494.5181 |  |  |  | 871.9811 | 23 | 0.5 |  | 69.0656 | 137.0074 | 1.2034
B-46 | 13 | 4022.4 | 40 | 0 | 0 | 802.9154 | 1389.3019 | 2502.8731 |  |  |  | 870.9878 | 23 | 0.5 |  | 68.0723 | 137.0074 | 1.2034
B-47 | 20.5 | 4042.9 | 50 | -1 | -0.35777 | 802.5577 | 1402.4771 | 2518.5716 |  |  | cruzar fence into milpas | 869.4214 | 23 | 0.5 |  | 66.8637 | 137.3652 | 1.2034
B-48 | 14 | 4056.9 | 50 | -1.5 | -0.36648 | 802.1912 | 1411.473 | 2529.2701 |  |  |  | 868.3517 | 23 | 0.5 |  | 66.1605 | 137.7317 | 1.2034
B-49 | 12 | 4068.9 | 50 | -4 | -0.83708 | 801.3541 | 1402.3029 | 2538.4203 |  |  | cruzar fence to houses/CASA 15 30m, 40* | 867.4348 | 23 | 0.5 |  | 66.0807 | 138.5688 | 1.2034
B-50 | 19 | 4087.9 | 140 | -5.5 | -1.8211 | 799.533 | 1387.3996 | 2550.5144 |  |  | CASA 16 10m, 50* | 865.9831 | 23 | 0.5 |  | 66.45 | 140.3898 | 1.2034
B-51 | 14 | 4101.9 | 142 | -8 | -1.9484 | 797.5846 | 1374.3719 | 2559.0027 |  |  | CASA 17 10m 56* | 864.9134 | 23 | 0.5 |  | 67.3287 | 142.3383 | 1.2034
B-52 | 10 | 4111.9 | 160 | -10 | -1.7365 | 795.8481 | 1380.7022 | 2562.3974 |  |  |  | 864.1493 | 23 | 0.5 |  | 68.3011 | 144.0747 | 1.2034
B-53 | 24 | 4135.9 | 50 | -7 | -2.9249 | 792.9233 | 1379.8708 | 2580.3807 |  |  | thru milpa | 862.3155 | 23 | 0.5 |  | 69.3922 | 146.9996 | 1.2034
B-54 | 15 | 4150.9 | 92 | -12 | -3.1187 | 789.8046 | 1377.323 | 2595.1206 |  |  |  | 861.1694 | 23 | 0.5 |  | 71.3648 | 150.1183 | 1.2034
B-55 | 24 | 4174.9 | 100 | -10.5 | -4.3737 | 785.431 | 1373.2252 | 2618.1957 |  |  |  | 859.3356 | 23 | 0.5 |  | 73.9046 | 154.4919 | 1.2034
B-56 | 19 | 4193.9 | 100 | -12.5 | -4.1124 | 781.3186 | 1370.0041 | 2636.1365 |  |  | entrar bosque | 857.8838 | 23 | 0.5 |  | 76.5652 | 158.6043 | 1.2034
B-57 | 19 | 4212.9 | 100 | -16.5 | -5.3963 | 775.9223 | 1360.8953 | 2654.0303 |  |  | bosque | 856.4321 | 23 | 0.5 |  | 80.5098 | 164.0006 | 1.2034
B-58 | 33 | 4245.9 | 120 | -17 | -9.6483 | 766.274 | 1345.1163 | 2681.6353 |  |  | 6m HG camino | 853.9106 | 23 | 0.5 |  | 87.6366 | 173.6488 | 1.2034
B-59 | 47 | 4292.9 | 120 | -15 | -12.1645 | 754.1095 | 1337.2329 | 2722.1155 |  |  | 6m HG/CASA 18 30m 240* | 850.3195 | 23 | 0.5 |  | 96.2099 | 185.8133 | 1.2034
B-60 | 31.5 | 4324.4 | 100 | -6 | -3.2926 | 750.8169 | 1326.5183 | 2752.3419 |  |  |  | 847.9126 | 23 | 0.5 |  | 97.0957 | 189.106 | 1.2034
B-61 | 45.5 | 4369.9 | 110 | -13 | -10.2353 | 740.5816 | 1311.3553 | 2794.5715 |  |  |  | 844.4361 | 23 | 0.5 |  | 103.8544 | 199.3413 | 1.2034
B-62 | 42.6 | 4412.5 | 110 | -9 | -6.6641 | 733.9175 | 1296.9646 | 2834.2128 |  |  |  | 841.1811 | 23 | 0.5 |  | 107.2636 | 206.0054 | 1.2034
B-63 | 37 | 4449.5 | 110 | -8 | -5.1494 | 728.7681 | 1284.433 | 2868.5996 |  |  | CASA 20 240m | 838.354 | 23 | 0.5 |  | 109.5859 | 211.1548 | 1.2034
B-64 | 25 | 4474.5 | 110 | -8.5 | -3.6952 | 725.0729 | 1286.588 | 2892.0883 |  |  | ultima CASA 19/ fin de dia | 836.4438 | 23 | 0.5 |  | 111.3709 | 214.85 | 1.2034
B-26 |  | 3457.4 | 0 | 0 |  | 874.4267 |  |  |  |  | RAMAL C | 914.1582 | 23 | 0.5 |  | 39.7314 | 65.4961 | 1.2034
C-1 | 20 | 3477.4 | 85 | 1 | 0.34905 | 874.7758 | 1288.6782 | 2911.8637 |  |  | C1-B26/ entrar milpa | 912.63 | 23 | 0.5 |  | 37.8542 | 65.1471 | 1.2034
C-2 | 20 | 3497.4 | 84 | -7 | -2.4374 | 872.3384 | 1292.8054 | 2931.3195 |  |  | thru milpa | 911.1019 | 23 | 0.5 |  | 38.7635 | 67.5845 | 1.2034
C-3 | 26.6 | 3524 | 78 | -12 | -5.5305 | 866.808 | 1296.4265 | 2956.6713 |  |  | CASA 21 10 m, 347* | 909.0694 | 23 | 0.5 |  | 42.2615 | 73.1149 | 1.2034
C-4 | 16.6 | 3540.6 | 82 | -13 | -3.7342 | 863.0738 | 1295.58 | 2972.473 |  |  | CASA 22 20m, 15* | 907.801 | 23 | 0.5 |  | 44.7273 | 76.8491 | 1.2034
C-5 | 13 | 3553.6 | 93 | -16 | -3.5833 | 859.4905 | 1296.8863 | 2984.8198 |  |  |  | 906.8077 | 23 | 0.5 |  | 47.3173 | 80.4324 | 1.2034
C-6 | 15 | 3568.6 | 84 | -18 | -4.6353 | 854.8552 | 1298.8717 | 2999.4116 |  |  | CASA 23 30m, 350* | 905.6616 | 23 | 0.5 |  | 50.8064 | 85.0676 | 1.2034
C-7 | 18 | 3586.6 | 82 | -12 | -3.7424 | 851.1128 | 1304.3124 | 3016.9089 |  |  | CASA 24 50m, 170* | 904.2863 | 23 | 0.5 |  | 53.1735 | 88.8101 | 1.2034
C-8 | 13 | 3599.6 | 72 | -11 | -2.4805 | 848.6323 | 1305.6463 | 3028.9054 |  |  | milpa | 903.293 | 23 | 0.5 |  | 54.6607 | 91.2906 | 1.2034
C-9 | 18.8 | 3618.4 | 84 | -14 | -4.5481 | 844.0842 | 1309.439 | 3046.9654 |  |  | CASA 25 30m, 0* | 901.8565 | 23 | 0.5 |  | 57.7723 | 95.8387 | 1.2034
C-10 | 18 | 3636.4 | 78 | -15 | -4.6587 | 839.4254 | 1313.0539 | 3063.7103 |  |  | CASA 26 30m, 348* | 900.4812 | 23 | 0.5 |  | 61.0558 | 100.4974 | 1.2034
C-11 | 15 | 3651.4 | 78 | -18 | -4.6353 | 834.7902 | 1316.0199 | 3077.7414 |  |  | CASA 27 30m, 182* | 899.3351 | 23 | 0.5 |  | 64.5449 | 105.1327 | 1.2034
C-12 | 33 | 3684.4 | 78 | -17 | -9.6483 | 825.1419 | 1324.7185 | 3107.8763 |  |  | thru milpa | 896.8136 | 23 | 0.5 |  | 71.6717 | 114.781 | 1.2034
C-13 | 19 | 3703.4 | 74 | -21 | -6.809 | 818.3329 | 1331.9332 | 3124.9272 |  |  | CASA 28 60m, 178*/ CASA 29 100m, 356* | 895.3619 | 23 | 0.5 |  | 77.0289 | 121.59 | 1.2034
C-14 | 19 | 3722.4 | 66 | -21 | -6.809 | 811.5239 | 1337.4145 | 3140.6583 |  |  | thru milpa | 893.9101 | 23 | 0.5 |  | 82.3862 | 128.399 | 1.2034
C-15 | 13 | 3735.4 | 72 | -25 | -5.494 | 806.0299 | 1342.5794 | 3152.2008 |  |  |  | 892.9168 | 23 | 0.5 |  | 86.8869 | 133.893 | 1.2034
C-16 | 17 | 3752.4 | 64 | -21 | -6.0923 | 799.9376 | 1348.267 | 3166.6479 |  |  | CASA 30 30m, 341* | 891.6179 | 23 | 0.5 |  | 91.6802 | 139.9852 | 1.2034
C-17 | 15 | 3767.4 | 69 | -19 | -4.8835 | 795.0541 | 1355.7828 | 3180.0397 |  |  |  | 890.4718 | 23 | 0.5 |  | 95.4176 | 144.8688 | 1.2034
C-18 | 13.5 | 3780.9 | 58 | -17 | -3.947 | 791.1071 | 1361.2388 | 3191.0449 |  |  | CASA 31 50m, 169* | 889.4403 | 23 | 0.5 |  | 98.3332 | 148.8158 | 1.2034
C-19 | 14.5 | 3795.4 | 65 | -16 | -3.9967 | 787.1103 | 1366.685 | 3203.6121 |  |  | CASA 32 60m, 350*/CASA 33 120m, 350* | 888.3323 | 23 | 0.5 |  | 101.222 | 152.8125 | 1.2034
C-20 | 18 | 3813.4 | 67 | -17 | -5.2627 | 781.8477 | 1374.7662 | 3219.2785 |  |  | CASA 34 60m, 15* | 886.957 | 23 | 0.5 |  | 105.1093 | 158.0752 | 1.2034
C-21 | 16 | 3829.4 | 62 | -19 | -5.2091 | 776.6386 | 1381.1597 | 3232.7884 |  |  |  | 885.7345 | 23 | 0.5 |  | 109.0959 | 163.2843 | 1.2034
C-22 | 14 | 3843.4 | 65 | -17 | -4.0932 | 772.5454 | 1386.175 | 3245.3204 |  |  |  | 884.6648 | 23 | 0.5 |  | 112.1194 | 167.3775 | 1.2034
C-23 | 16.3 | 3859.7 | 68 | -9 | -2.5499 | 769.9955 | 1390.3418 | 3260.3209 |  |  |  | 883.4193 | 23 | 0.5 |  | 113.4238 | 169.9274 | 1.2034
C-24 | 18.4 | 3878.1 | 75 | -7 | -2.2424 | 767.7531 | 1392.2508 | 3277.921 |  |  |  | 882.0134 | 23 | 0.5 |  | 114.2603 | 172.1698 | 1.2034
C-25 | 9.6 | 3887.7 | 84 | -8 | -1.3361 | 766.417 | 1395.9653 | 3287.432 |  |  | C25-E1 | 881.2799 | 23 | 0.5 |  | 114.8629 | 173.5059 | 1.2034
C-26 | 28.5 | 3916.2 | 67 | -5 | -2.4839 | 763.9331 | 1404.2662 | 3313.5227 |  |  | CASA 35 40m, 351* | 879.1023 | 23 | 0.5 |  | 115.1692 | 175.9898 | 1.2034
C-27 | 21 | 3937.2 | 73 | -6 | -2.1951 | 761.738 | 1412.0899 | 3333.5287 |  |  | se sale milpa | 877.4977 | 23 | 0.5 |  | 115.7597 | 178.1849 | 1.2034
C-28 | 45.5 | 3982.7 | 68 | -5 | -3.9656 | 757.7724 | 1416.0404 | 3375.1962 |  |  | CASA 36 20m, 1* | 874.0212 | 23 | 0.5 |  | 116.2488 | 182.1505 | 1.2034
C-29 | 40 | 4022.7 | 85 | -9 | -6.2574 | 751.515 | 1416.7299 | 3415.0379 |  |  | CASA 37 60m, 355* | 870.9648 | 23 | 0.5 |  | 119.4498 | 188.4079 | 1.2034
C-30 | 74 | 4096.7 | 89 | 1 | 1.2915 | 752.8065 | 1419.312 | 3488.9815 |  |  |  | 865.3107 | 23 | 0.5 |  | 112.5042 | 187.1164 | 1.2034
C-31 | 44 | 4140.7 | 88 | 2 | 1.5356 | 754.3421 | 1426.9479 | 3532.9547 |  |  | entrar milpa | 861.9487 | 23 | 0.5 |  | 107.6067 | 185.5808 | 1.2034
C-32 | 16 | 4156.7 | 80 | 0 | 0 | 754.3421 | 1429.7263 | 3548.6733 |  |  |  | 860.7262 | 23 | 0.5 |  | 106.3841 | 185.5808 | 1.2034
C-33 | 15 | 4171.7 | 80 | -4 | -1.0463 | 753.2957 | 1433.3463 | 3563.3892 |  |  |  | 859.5801 | 23 | 0.5 |  | 106.2844 | 186.6271 | 1.2034
C-34 | 29 | 4200.7 | 76 | -5 | -2.5275 | 750.7682 | 1449.5011 | 3591.1813 |  |  | CASA 38 20m, 184* | 857.3643 | 23 | 0.5 |  | 106.596 | 189.1547 | 1.2034
C-35 | 18 | 4218.7 | 56 | -9 | -2.8158 | 747.9524 | 1457.8476 | 3605.3736 |  |  |  | 855.9889 | 23 | 0.5 |  | 108.0365 | 191.9705 | 1.2034
C-36 | 14 | 4232.7 | 62 | -18 | -4.3262 | 743.6262 | 1456.4558 | 3617.5471 |  |  |  | 854.9192 | 23 | 0.5 |  | 111.2931 | 196.2967 | 1.2034
C-37 | 22 | 4254.7 | 96 | -10 | -3.8203 | 739.8059 | 1456.4558 | 3639.2635 |  |  | chorro para escuela 182*, 15m | 853.2382 | 23 | 0.5 |  | 113.4323 | 200.117 | 1.2034
C-38 | 20 | 4274.7 | 90 | -7 | -2.4374 | 737.3685 | 1438.7685 | 3659.1714 |  |  | ultima CASA 39 | 851.7101 | 23 | 0.5 |  | 114.3416 | 202.5544 | 1.2034
B-26 |  | 3457.4 | 0 | 0 |  | 874.4267 |  |  |  |  | RAMAL D | 914.1582 | 23 | 0.5 |  | 39.7314 | 65.4961 | 1.2034
D-1 | 19 | 3476.4 | 153 | -5.5 | -1.8211 | 872.6057 | 1422.3898 | 3667.6388 |  |  | D1-B26/ arbol de aguacate/entrar milpa | 912.7064 | 23 | 0.5 |  | 40.1007 | 67.3172 | 1.2034
D-2 | 21 | 3497.4 | 150 | -11 | -4.007 | 868.5987 | 1405.2999 | 3677.9093 |  |  | milpa | 911.1019 | 23 | 0.5 |  | 42.5032 | 71.3242 | 1.2034
D-3 | 21 | 3518.4 | 146 | -12 | -4.3661 | 864.2325 | 1388.2705 | 3689.1393 |  |  | milpa | 909.4973 | 23 | 0.5 |  | 45.2648 | 75.6903 | 1.2034
D-4 | 18 | 3536.4 | 146 | -17 | -5.2627 | 858.9699 | 1375.0842 | 3698.4718 |  |  | abustos | 908.122 | 23 | 0.5 |  | 49.1521 | 80.953 | 1.2034
D-5 | 20 | 3556.4 | 140 | -22 | -7.4921 | 851.4777 | 1360.0821 | 3710.3914 |  |  | bosque | 906.5938 | 23 | 0.5 |  | 55.1161 | 88.4452 | 1.2034
D-6 | 15 | 3571.4 | 144 | -22 | -5.6191 | 845.8586 | 1348.2876 | 3718.6765 |  |  |  | 905.4477 | 23 | 0.5 |  | 59.5891 | 94.0643 | 1.2034
D-7 | 18 | 3589.4 | 148 | -20 | -6.1564 | 839.7023 | 1333.6393 | 3727.5205 |  |  |  | 904.0723 | 23 | 0.5 |  | 64.3701 | 100.2206 | 1.2034
D-8 | 28 | 3617.4 | 150 | -22 | -10.489 | 829.2133 | 1311.1563 | 3741.3481 |  |  |  | 901.9329 | 23 | 0.5 |  | 72.7197 | 110.7096 | 1.2034
D-9 | 19 | 3636.4 | 150 | -9 | -2.9723 | 826.241 | 1294.4356 | 3750.7773 |  |  |  | 900.4812 | 23 | 0.5 |  | 74.2402 | 113.6819 | 1.2034
D-10 | 18 | 3654.4 | 153 | -7 | -2.1936 | 824.0474 | 1279.452 | 3758.9044 |  |  |  | 899.1058 | 23 | 0.5 |  | 75.0585 | 115.8755 | 1.2034
D-11 | 23 | 3677.4 | 147 | 6 | 2.4042 | 826.4515 | 1262.9978 | 3771.4006 |  |  | se sale bosque | 897.3485 | 23 | 0.5 |  | 70.8969 | 113.4714 | 1.2034
D-12 | 38 | 3715.4 | 136 | 4 | 2.6507 | 829.1023 | 1230.5048 | 3797.3966 |  |  |  | 894.445 | 23 | 0.5 |  | 65.3427 | 110.8206 | 1.2034
D-13 | 22 | 3737.4 | 149 | 10 | 3.8203 | 832.9225 | 1214.9198 | 3808.6998 |  |  | entrar otro bosque | 892.764 | 23 | 0.5 |  | 59.8415 | 107.0003 | 1.2034
D-14 | 20 | 3757.4 | 136 | -4 | -1.3951 | 831.5274 | 1201.0604 | 3822.3377 |  |  |  | 891.2358 | 23 | 0.5 |  | 59.7084 | 108.3955 | 1.2034
D-15 | 14 | 3771.4 | 134 | -11 | -2.6713 | 828.8561 | 1191.6879 | 3832.0653 |  |  |  | 890.1661 | 23 | 0.5 |  | 61.3101 | 111.0668 | 1.2034
D-16 | 17 | 3788.4 | 133 | -15 | -4.3999 | 824.4562 | 1178.9266 | 3843.9551 |  |  |  | 888.8672 | 23 | 0.5 |  | 64.411 | 115.4667 | 1.2034
D-17 | 18 | 3806.4 | 141 | -17 | -5.2627 | 819.1935 | 1168.3289 | 3854.8968 |  |  |  | 887.4919 | 23 | 0.5 |  | 68.2984 | 120.7294 | 1.2034
D-18 | 13 | 3819.4 | 128 | -15 | -3.3646 | 815.8288 | 1158.17 | 3864.1812 |  |  |  | 886.4986 | 23 | 0.5 |  | 70.6697 | 124.0941 | 1.2034
D-19 | 18 | 3837.4 | 144 | -25 | -7.6071 | 808.2217 | 1145.492 | 3874.2435 |  |  |  | 885.1232 | 23 | 0.5 |  | 76.9015 | 131.7012 | 1.2034
D-20 | 15 | 3852.4 | 141 | -18 | -4.6353 | 803.5864 | 1136.7091 | 3883.6833 |  |  |  | 883.9771 | 23 | 0.5 |  | 80.3907 | 136.3364 | 1.2034
D-21 | 14 | 3866.4 | 128 | 0 | 0 | 803.5864 | 1129.4986 | 3894.7138 |  |  |  | 882.9074 | 23 | 0.5 |  | 79.321 | 136.3364 | 1.2034
D-22 | 14 | 3880.4 | 121 | -1 | -0.24433 | 803.3421 | 1122.4996 | 3906.6684 |  |  |  | 881.8377 | 23 | 0.5 |  | 78.4956 | 136.5808 | 1.2034
D-23 | 18 | 3898.4 | 120 | -5 | -1.5688 | 801.7733 | 1112.4725 | 3922.1715 |  |  |  | 880.4623 | 23 | 0.5 |  | 78.689 | 138.1496 | 1.2034
D-24 | 17 | 3915.4 | 124 | -6 | -1.777 | 799.9963 | 1103.0183 | 3936.2115 |  |  | salir bosque | 879.1634 | 23 | 0.5 |  | 79.1671 | 139.9266 | 1.2034
D-25 | 41 | 3956.4 | 124 | -5 | -3.5734 | 796.4229 | 1085.1134 | 3969.3309 |  |  |  | 876.0307 | 23 | 0.5 |  | 79.6078 | 143.5 | 1.2034
D-26 | 43 | 3999.4 | 116 | 13 | 9.6729 | 806.0958 | 1061.6844 | 4006.0874 |  |  |  | 872.7451 | 23 | 0.5 |  | 66.6493 | 133.8271 | 1.2034
D-27 | 28 | 4027.4 | 124 | 18 | 8.6525 | 814.7483 | 1046.0319 | 4028.9478 |  |  |  | 870.6057 | 23 | 0.5 |  | 55.8574 | 125.1746 | 1.2034
D-28 | 42 | 4069.4 | 126 | 10 | 7.2932 | 822.0415 | 1020.002 | 4059.9889 |  |  |  | 867.3966 | 23 | 0.5 |  | 45.3551 | 117.8814 | 1.2034
D-29 | 42 | 4111.4 | 129 | 24 | 17.0829 | 839.1245 | 994.3282 | 4091.3646 |  |  |  | 864.1875 | 23 | 0.5 |  | 25.063 | 100.7984 | 1.2034
D-30 | 21 | 4132.4 | 132 | 16 | 5.7884 | 844.9128 | 980.8208 | 4106.9113 |  |  | fence/ CASA 40 60m, 32*/CASA 41 100m, 74*/ CASA 42 18m, 202* (mas 8 orientacion) | 862.5829 | 23 | 0.5 |  | 17.6701 | 95.01 | 1.2034
D-31 | 16 | 4148.4 | 132 | -5 | -1.3945 | 843.5183 | 970.5754 | 4118.6552 |  |  | entrar milpa | 861.3604 | 23 | 0.5 |  | 17.842 | 96.4045 | 1.2034
D-32 | 19 | 4167.4 | 130 | -9 | -2.9723 | 840.5461 | 961.4774 | 4132.7141 |  |  | milpa | 859.9086 | 23 | 0.5 |  | 19.3625 | 99.3768 | 1.2034
D-33 | 18 | 4185.4 | 119 | -15 | -4.6587 | 835.8874 | 951.7549 | 4147.5079 |  |  | CASA 43 50m, 44* | 858.5333 | 23 | 0.5 |  | 22.646 | 104.0355 | 1.2034
D-34 | 20 | 4205.4 | 124 | -20 | -6.8404 | 829.0469 | 939.9275 | 4162.7705 |  |  |  | 857.0051 | 23 | 0.5 |  | 27.9582 | 110.8759 | 1.2034
D-35 | 13 | 4218.4 | 129 | -23 | -5.0795 | 823.9674 | 939.5099 | 4172.5292 |  |  | salir milpa/fence/CASA 44 20m, 27* | 856.0118 | 23 | 0.5 |  | 32.0444 | 115.9554 | 1.2034
D-36 | 31 | 4249.4 | 92 | -15 | -8.0234 | 815.9441 | 969.4536 | 4203.5103 |  |  |  | 853.6432 | 23 | 0.5 |  | 37.6991 | 123.9788 | 1.2034
C-25 | 0 | 3887.7 |  |  |  | 766.417 |  |  |  |  | RAMAL E | 881.2799 | 23 | 0.5 |  | 114.8629 | 173.5059 | 1.2034
E-1 | 10 | 3897.7 | 140 | -5 | -0.87156 | 765.5455 | -9.1007 | 6.4191 |  |  | E1-C25/ entrar milpa | 880.5158 | 23 | 0.5 |  | 114.9704 | 174.3774 | 1.2034
E-2 | 11 | 3908.7 | 156 | -3 | -0.5757 | 764.9698 | -19.2857 | 10.8904 |  |  | CASA 45 20m, 74* | 879.6753 | 23 | 0.5 |  | 114.7056 | 174.9531 | 1.2034
E-3 | 13 | 3921.7 | 158 | -2 | -0.45369 | 764.5161 | -30.7571 | 15.7574 |  |  | CASA 46 20m, 76* | 878.682 | 23 | 0.5 |  | 114.166 | 175.4068 | 1.2034
E-4 | 11 | 3932.7 | 152 | -2 | -0.38389 | 764.1322 | -39.9768 | 20.9184 |  |  |  | 877.8415 | 23 | 0.5 |  | 113.7094 | 175.7907 | 1.2034
E-5 | 11 | 3943.7 | 147 | -2 | -0.38389 | 763.7483 | -48.2736 | 26.8866 |  |  | CASA 47 15m, 71* | 877.0011 | 23 | 0.5 |  | 113.2528 | 176.1746 | 1.2034
E-6 | 11 | 3954.7 | 139 | 5 | 0.95871 | 764.707 | -57.7636 | 33.9707 |  |  | milpa | 876.1606 | 23 | 0.5 |  | 111.4536 | 175.2159 | 1.2034
E-7 | 11 | 3965.7 | 150 | 11 | 2.0989 | 766.8059 | -65.531 | 39.4297 |  |  |  | 875.3201 | 23 | 0.5 |  | 108.5142 | 173.117 | 1.2034
E-8 | 11 | 3976.7 | 136 | 7 | 1.3406 | 768.1465 | -73.5159 | 47.0663 |  |  | CASA 48 40m, 70* | 874.4796 | 23 | 0.5 |  | 106.3331 | 171.7764 | 1.2034
E-9 | 12 | 3988.7 | 137 | 2 | 0.41879 | 768.5653 | -84.7853 | 55.2303 |  |  | CASA 49 20m, 61*/ CASA 50 50m, 61* | 873.5627 | 23 | 0.5 |  | 104.9975 | 171.3576 | 1.2034
E-10 | 13 | 4001.7 | 160 | 4 | 0.90683 | 769.4721 | -97.5566 | 59.6759 |  |  | CASA 51 40m, 258* | 872.5694 | 23 | 0.5 |  | 103.0973 | 170.4508 | 1.2034
E-11 | 11 | 4012.7 | 170 | 1 | 0.19198 | 769.6641 | -108.4479 | 61.5858 |  |  |  | 871.7289 | 23 | 0.5 |  | 102.0649 | 170.2588 | 1.2034
E-12 | 15 | 4027.7 | 172 | 1 | 0.26179 | 769.9259 | -123.1179 | 63.6734 |  |  | CASA 52 30m, 64* | 870.5828 | 23 | 0.5 |  | 100.657 | 169.997 | 1.2034
E-13 | 14 | 4041.7 | 168 | 0 | 0 | 769.9259 | -137.0987 | 66.5837 |  |  | CASA 53 20m, 70* | 869.5131 | 23 | 0.5 |  | 99.5872 | 169.997 | 1.2034
E-14 | 14 | 4055.7 | 177 | -1 | -0.24433 | 769.6815 | -150.6196 | 67.3159 |  |  |  | 868.4434 | 23 | 0.5 |  | 98.7619 | 170.2414 | 1.2034
E-15 | 8 | 4063.7 | 165 | 2 | 0.2792 | 769.9607 | -158.5843 | 69.3852 |  |  | milpa | 867.8321 | 23 | 0.5 |  | 97.8714 | 169.9622 | 1.2034
E-16 | 12 | 4075.7 | 175 | 2 | 0.41879 | 770.3795 | -170.1684 | 70.4305 |  |  |  | 866.9152 | 23 | 0.5 |  | 96.5357 | 169.5434 | 1.2034
E-17 | 12 | 4087.7 | 165 | -2 | -0.41879 | 769.9607 | -158.1757 | 73.5363 |  |  | ultima CASA 54 | 865.9983 | 23 | 0.5 |  | 96.0376 | 169.9622 | 1.2034
Note on Q4: minimum 10 m at each house
Note on S4: between 0.7 and 2 m/s
Note on R4: maximum 40 m (taps) maximum 100m (network)

## Tanque Distrib
Storage Tank Calculation Sheet |  |  |  | Date | 18/10/2007
Written by Pablo Gamarra
Aldea |  | KALAMPATZOM
Data | Unit | Inputs
Spring Flow | (l/s) | 1.1
Families |  | 92
Population |  | 460
Project Life | (years) | 20
Growth Rate | (%) | 3
Water use per person | (l/day) | 80
Peak Factor |  | 10
|  | Now | Project | Max
Year |  | 2006 | 2026 | 2038.1556
Life | (years) | 0 | 20 | 32.1556
Families |  | 92 | 167 | 238
Persons per family |  | 5 | 4.976 | 5.0042
Population |  | 460 | 831 | 1191
Water Use | (l/p/day) | 80 | 80 | 80
Village Requirement | (l/day) | 36800 | 66480 | 95280
Spring Volume | (l/day) | 95040 | 95040 | 95040
Mean Use Rate | (l/s) | 0.42593 | 0.76944 | 1.1028
Peak flow from tank | (l/s) | 4.2593 | 7.6944 | 11.0278
Tank size Needed |  | 2006 | 2026 | 2038.1556
Min size (peak factor) | (m^3) | 4.6967 | 10.88 | 16.88
General System - Ixil | (m^3) | 0 | 11.04 | 39.84
Lavadero System - Ixil | (m^3) | 0 | 17.4864 | 39.84
Jordan's | (m^3) | 3.12 | 18.96 | 47.76
Notes
1. The min size tank calculation is based on the 15 min peak factor (ie. the min sized tank needed to meet this peak.)
2. The General and Lavadero systems are based on patterns recorded in typical aldeas in the Ixil in May 98
3. The Jordan's method is based on the standard 30%/40%/30% pattern in his book, recorded in Nepal in the 70s
Calculations
2. General system |  |  |  |  | 2006 |  | 2026 |  | 2038.1556
Hour | %use | No.hours | Cum Hours | Spring in | Cum. Use | Difference | Cum. Use | Difference | Cum. Use | Difference
5 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5-8 | 0.17 | 3 | 3 | 11880 | 6256 | 5624 | 11301.6 | 578.4 | 16197.6 | -4317.6
8-9 | 0.11 | 1 | 4 | 15840 | 10304 | 5536 | 18614.4 | -2774.4 | 26678.4 | -10838.4
9-1 | 0.3 | 4 | 8 | 31680 | 21344 | 10336 | 38558.4 | -6878.4 | 55262.4 | -23582.4
1-3 | 0.18 | 2 | 10 | 39600 | 27968 | 11632 | 50524.8 | -10924.8 | 72412.8 | -32812.8
3-7 | 0.24 | 4 | 14 | 55440 | 36800 | 18640 | 66480 | -11040 | 95280 | -39840
7-5 | 0 | 10 | 24 | 95040 | 36800 | 58240 | 66480 | 28560 | 95280 | -240
total | 1 | 24 |  |  | Storage | 0 |  | -11040 |  | -39840
3. Lavadero system |  |  |  |  | 2006 |  | 2026 |  | 2038.1556
Hour | %use | No.hours | Cum Hours | Spring in | Cum. Use | Difference | Cum. Use | Difference | Cum. Use | Difference
5 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5-8 | 0.18 | 3 | 3 | 11880 | 6624 | 5256 | 11966.4 | -86.4 | 17150.4 | -5270.4
8-9 | 0.2 | 1 | 4 | 15840 | 13984 | 1856 | 25262.4 | -9422.4 | 36206.4 | -20366.4
9-10 | 0.14 | 1 | 5 | 19800 | 19136 | 664 | 34569.6 | -14769.6 | 49545.6 | -29745.6
10-12 | 0.16 | 2 | 7 | 27720 | 25024 | 2696 | 45206.4 | -17486.4 | 64790.4 | -37070.4
12-7 | 0.32 | 7 | 14 | 55440 | 36800 | 18640 | 66480 | -11040 | 95280 | -39840
7-5 | 0 | 10 | 24 | 95040 | 36800 | 58240 | 66480 | 28560 | 95280 | -240
total | 1 | 24 |  |  | Storage | 0 |  | -17486.4 |  | -39840
4. Jordan's system |  |  |  |  | 2006 |  | 2026 |  | 2038.1556
Hour | %use | No.hours | Cum Hours | Spring in | Cum. Use | Difference | Cum. Use | Difference | Cum. Use | Difference
6 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6-8 | 0.3 | 2 | 2 | 7920 | 11040 | -3120 | 19944 | -12024 | 28584 | -20664
8-16 | 0.4 | 8 | 10 | 39600 | 25760 | 13840 | 46536 | -6936 | 66696 | -27096
16-18 | 0.3 | 2 | 12 | 47520 | 36800 | 10720 | 66480 | -18960 | 95280 | -47760
18-6 | 0 | 12 | 24 | 95040 | 36800 | 58240 | 66480 | 28560 | 95280 | -240
total | 1 | 24 |  |  | Storage | -3120 |  | -18960 |  | -47760